## Slide 1
Nikolay VOUTCHKOV,PE, BCEE
International Consulting
Services
Presentation for
Asian Development Bank
November, 2014
Overview of Desalination Trends and Jaffna Project

## Slide 2: Desalination – Where Are We Today?
Chart: 
| RO | Thermal | ED | Other
Technology | 0.6 | 0.34 | 0.035 | 0.02
16,000 Desalination Plants Worldwide –
66.4 Million m³/day
Source: IDA Desalination Yearbook 2013-2014

## Slide 3: Desalination Market Drivers
Water Scarcity
Economic Growth
Population Growth

## Slide 4: Membrane Desalination – Key Trends
SWRO Desalination Most Commonly Used
Large - (over 60 MLD) and Mega - (over 200 MLD) Desalination Plants Are the Wave of the Future
Most Large Urban Coastal Centers Worldwide Have Established a Target to Produce 25% of their Drinking Water from Desalination
Research &Development Activities are in 10-Year High – Likely to Yield Breakthroughs in Membrane and Desalination Technologies by 2015
Large SWRO Projects Are Aiming at Sustainability – Use of Alternative Power Supply Sources is On the Rise

## Slide 5: Water Production Costs (Medium & Large SWRO Plants)
Classification | Cost of Water Production (US$/m³)
Low-End Bracket | 0.5 – 0.8
Medium Range | 1.0 - 1.5
High-End Bracket | 2.0 – 4.0
Average | 1.0

## Slide 6: Main Factors Affecting Costs
Plant Size – Bigger is Better
Source Water Quality - TDS, Temperature, Solids, Silt and Organics Content
Product Water Quality – TDS, Boron, Bromides, Disinfection Compatibility
Concentrate Disposal Method
Power Supply & Unit Power Costs
Project Delivery Method & Financing
Other Factors:
  Intake and Discharge System Type
  Pretreatment & RO System Design
  Plant Capacity Availability Target
Notes: 6

## Slide 7: Plant Size and Construction Costs

## Slide 8: Water Production Costs of Recent SWRO Desalination Projects
Chart: Cost of Water , US$/m³
| 400 MLD Sorek, Israel | 500 MLD Mactaa, Algeria | 330 MLD Hadera, Israel | 360 MLD Askelon, Israel | 2 MLD MGD Sand City, CA | 200 MLD Hamma, Algeria | 95 MlD Tampa Bay, FL | 170 MLD Fujairah, UAE | 190 MLD Carlsbad, CA | 200 MLD Barcelona, Spain | 140 MLD Perth I, Australia | 250 MLD Sydney, Australia | 150 MLD Perth II, Australia | 410 MLD Melbourne, Australia | 130 MlD Gold Coast, Australia | 300 MLD Adelaide, Australia
Cost of Water US$/m3 | 0.53 | 0.56 | 0.6 | 0.61 | 0.77 | 0.83 | 0.92 | 0.94 | 1.15 | 1.16 | 1.16 | 1.93 | 2.2 | 2.5 | 2.9 | 3

## Slide 9: Key Reasons for Cost Disparity Between High-End & Low-end Cost Projects
Desalination Site Location (NIMBI vs. Science Driven)
  Costly Plants Have Overly Long Product Water Delivery Pipelines
    120 MGD Melbourne Plant – Cost of Plant/Delivery + Power Supply Systems =
    US$1.7 BB/1.1 BB (50 miles)
    66 MGD Sydney SWRO Plant – Cost of Plant/Delivery System
    = US$560 MM/US$490 MM (10 miles of underground tunnel under Botany Bay).
Environmental Considerations
  Complex Intakes & Diffuser Systems
Phasing Strategy
  Intake and Discharge System Capacity
  Pretreatment & RO System Design
Labor Market Pressures
Method of Project Delivery & Risk Allocation
Notes: 9

## Slide 10: Energy Use for Membrane Desalination (Medium & Large SWRO Plants)
Classification | SWRO System Energy Use (kWh/m³)
Low-End Bracket | 2.5 – 2.8
Medium Range | 3.0 – 3.5
High-End Bracket | 4.0 – 4.5
Average | 3.0

## Slide 11
24 MLD Jaffna SWRO Plant
Preliminary Feasibility Analysis
TA-8668 SRI: Rapid Assessment of Seawater Desalination and Other Alternative Water Sources for Jaffna Water Supply

## Slide 12: Present Desalination Project Status
Six Alternative Sites in Jaffna Identified and Visited in September 2014
Two Sites Selected After Preliminary Screening:
  Martuthankerni/Pallai
  Kankesanthurai/Keerimalai
Initial Feasibility Evaluation Completed – Both Sites Fund Feasible
Draft Feasibility Study Submitted to ADB for Review in October, 2014

## Slide 13: Martuthankerni/Pallai Site

## Slide 14: Kankesanthurai/Keerimalai

## Slide 15: Recommended Desalination Plant Configuration

## Slide 16: Plant Intake and Outfall

## Slide 17: Concentrate Disposal
Outfall with Diffusers Designed
to Reduce Salinity Down to 10%
of Ambient Levels within 100 m of the Discharge

## Slide 18: Gravity and Pressure Pretreatment Filters in Series
Stage 1 Pretreatment
Gravity Filters with Anthracite & Sand
to Remove
Algae, Coarse Solids and Suspended
Organics
Stage 2 Pretreatment
Pressure Filters to Remove
Fine Solids & Silt

## Slide 19: RO Trains and Energy Recovery System
Provides 48% of the Energy
Provides 2 % of the Energy
Provides 50% of the Energy
8 SWRO Trains Operating 20 hrs
per Day to Avoid Peak Power Tariff
8 Pressure Exchanger Trains
(one Per SWRO Train)
4 - ERI/PX-Q200 Units per Train
Energy Recovery Efficiency – 97%

## Slide 20: Summary of Plant Energy Use and Costs
Parameter | Martuthankerni/Pallai | Kankesanthurai/ Keermalai
Average Energy Use, kWh/m³ RO System Total Plant (w/o Delivery) | 2.27 3.20 | 2.27 3.33
Total Plant Power Demand, MW | 3.84(avg.)/4.80 (max) | 4.00 (avg.)/4.97 (max)
Capital Costs, in million US$ | 46.3 | 48.1
Annual O&M Costs, in million US$/year | 3.76 | 3.85
Annualized Capital Costs, US$/m³ (20 years loan @ 6 %) | 0.46 | 0.48
Annual O&M Costs, US$/m³ | 0.43 | 0.44
Total Cost of Water Production, US$/m³ | 0.89 | 0.92

## Slide 21: Jaffna Desalination Plant – Capital Cost Breakdown
Intake – 12%
of CC
Post-treatment –
3% of CC
RO System –
36% of CC
Pretreatment –
13% of CC
Total Capital Cost
US$46.3 – 48.1 MM
Construction Cost (CC)
US$34.6 – 36.0 MM
Storage Tank –
5% of CC
Discharge Outfall –
8% of CC
Other Costs
– 35% of CC
Notes: 21

## Slide 22: Energy Use of the Jaffna SWRO Plant
Intake – 10%
(0.3 kWh/m³)
Product Water Delivery
2%
RO System –
74%
Pretreatment –
6%
(0.15 kWh/m³)
(2.4 kWh/m³)
(0.1 kWh/m³)
Other Facilities
8%
(0.25 kWh/m³)
Total Energy Use
3.20-3.33 kWh/m³
For TDS = 32 ppt &
Temp. = 29°C
Notes: 22

## Slide 23: Jaffna SWRO Project O&M Cost Breakdown
Chart: 
| Energy | Chemicals | RO/CF Replacement | Other Costs | Labor | Maintenance | Insurance | Operator Training
O&M Costs (%) | 53 | 11.5 | 6.4 | 7.9 | 12.6 | 6.4 | 1.1 | 1.1
O&M Cost
US$0.43 – 0.44/m³

## Slide 24: Selected Desalination Plant Sites

## Slide 25: Water Delivery Systems from the Two Alternative Sites

## Slide 26: Comparison of Costs for Water Production and Delivery from the Two Sites
Item | Capital Cost |  | Annual O&M Cost |  | Total Cost of Water
 | US$ million | Amortized US$/m³ | US$ Million/yr. | US$/m³ | US$/m³
Martuthankeri – Plant | 46.3 | 0.460 | 3.76 | 0.430 | 0.890
Martuthankeri - Conveyance | 32.6 | 0.324 | 0.55 | 0.062 | 0.386
Martuthankeri – Total System | 78.9 | 0.784 | 4.31 | 0.492 | 1.276
Kankesanthurai – Plant | 48.1 | 0.480 | 3.85 | 0.440 | 0.920
Kankesanthurai – Conveyance | 23.2 | 0.231 | 0.36 | 0.041 | 0.272
Kankesanthurai – Total System | 71.4 | 0.711 | 4.44 | 0.481 | 1.192

## Slide 27: General Project Delivery Schedule

## Slide 28: Next Project Implementation Steps
Completion of Environmental Impact Assessment & Additional Studies – 3 months (by Jan 2015)
Development of Contractor Procurement Documents – 3 Months (by Jan 2015)
Contractor Procurement & Selection – 4 months (by April 2015)
Land Acquisition – 6 months (by April 2015)
Project Funding (by July 2015)
Construction Begins – August 2015
Plant in Operation – September 2017

## Slide 29: Concluding Remarks
Seawater Reverse Osmosis Desalination is Proven Technology with Over 20 Years of Worldwide Experience
Jaffna Desalination Project is Feasible
O&M Costs for the Fresh Water Production – US$0.43-0.44/m³
Project Capital Cost – US$46 to 48 million
Project Construction Period – 24 months
If Contractor Procured by April, 2014 the Plant Can be Operational by the Fall of 2017
Notes: 29

## Slide 30: Questions ?
Nikolay Voutchkov
Nikolay Voutchkov, PE, BCEE
Water Globe Consulting
nvoutchkov@water-g.com